## SAFE Volume Calculator
ROXUL SAFE® Volume Calculator
Last Updated: July 1, 2022
The intention of this tool is to provide the ROCKWOOL Sales Team with the recommended SAFE material and an estimated volume for perimeter fire containment systems
CALCULATOR INPUTS
| Evaluation Criteria | Perimeter Area
A | Number of storeys require perimeter fire system | 15 | please complete
B | Length of each floor perimeter fire system (ft.) | 400 | please complete
C | Width of each floor perimeter fire system (ft.) | 400 | please complete
D | Width of perimeter joint (in.) | 4 | please complete
E | Depth of floor slab (in.) | 4 | please complete
F | % insulation compression required | 25% | please complete
CALCULATOR OUTPUTS
| SAFE Product | Thickness Required (exact compression) | Thickness Required (nearest available material) | Safing Strips | Pcs/ Bd. | Perimeter / Floor (ft.) | Total Perimeter (ft.) | Strips Required | Boards Required | Boards / PAL | Min. Order Qty (Boards) | Min. Order Qty (PAL) | PALs Required*
| 325160- ROXUL SAFE 6" x 24" x 48" | 5.33 | 6 | 6-4 | 6 | 1600 | 24000 | 6000 | 1000 | 30 | 30 | 1 | 34
*PALs required calculates the amount of pallets required to service the project subject to minimum order quantities of each material
Assumptions:
- Model assumes that the installer is using all off cuts as the analysis is based on the total amount of product required to fill the perimeter safing slot
- Each floor is presumed to have an identical length and width, if that varies, user would need to either adjust to part of a floor or copy the chart and replicate for floors of the same size
- Specific volume is always dependent on the ASTM E2307 tested system being installed
- Estimates presume that the floor edge is straight, for additional clarification please confirm with the project architect, engineer and/or consultant for more details
- Refer to the specific tested designs for the volume and compression requirements of that system

## Reference
Strip | Strips | Board Size | Material | Pcs/Bd. | Boards/PAL | Min. Boards | Min. PAL | Thicknesses | Next Thickness |  | Table must remain in order of thicknesses from thinnest to thickest
1.5-4 | 1.5" x 4" x 48" | 1.5" x 24" x 48" | 325089- ROXUL SAFE 1.5" x 24" x 48" | 6 | 120 | 120 | 1 | 1.5 | 2
2-4 | 2" x 4" x 48" | 2" x 24" x 48" | 168733 - ROXUL SAFE 2" x 24" x 48" | 6 | 96 | 96 | 1 | 2 | 3
3-4 | 3" x 4" x 48" | 3" x 24" x 48" | 168734 - ROXUL SAFE 3" x 24" x 48" | 6 | 60 | 60 | 1 | 3 | 4
3-6 | 3" x 6" x 48" | 3" x 24" x 48" | 168734 - ROXUL SAFE 3" x 24" x 48" | 4 | 60 | 60 | 1 | 3 | 4
4-4 | 4" x 4" x 48" | 4" x 24" x 48" | 168735 - ROXUL SAFE 4" x 24" x 48" | 6 | 48 | 48 | 1 | 4 | 5
4-6 | 4" x 6" x 48" | 4" x 24" x 48" | 168735 - ROXUL SAFE 4" x 24" x 48" | 4 | 48 | 48 | 1 | 4 | 5
5-4 | 5" x 4" x 48" | 5" x 24" x 48" | 325093- ROXUL SAFE 5" x 24" x 48" | 6 | 36 | 468 | 13 | 5 | 6
6-4 | 6" x 4" x 48" | 6" x 24" x 48" | 325160- ROXUL SAFE 6" x 24" x 48" | 6 | 30 | 30 | 1 | 6 | n/a
Joint Width (in) | % Compression of the slab edge insulation & thickness required to meet joint width
| 10% | 15% | 20% | 25% | 30% | 33% | 35% | 40% | 45% | 50%
0.5 | 0.56 | 0.59 | 0.63 | 0.67 | 0.71 | 0.75 | 0.77 | 0.83 | 0.91 | 1
1 | 1.11 | 1.18 | 1.25 | 1.33 | 1.43 | 1.49 | 1.54 | 1.67 | 1.82 | 2
1.5 | 1.67 | 1.76 | 1.88 | 2 | 2.14 | 2.24 | 2.31 | 2.5 | 2.73 | 3
2 | 2.22 | 2.35 | 2.5 | 2.67 | 2.86 | 2.99 | 3.08 | 3.33 | 3.64 | 4
2.5 | 2.78 | 2.94 | 3.13 | 3.33 | 3.57 | 3.73 | 3.85 | 4.17 | 4.55 | 5
3 | 3.33 | 3.53 | 3.75 | 4 | 4.29 | 4.48 | 4.62 | 5 | 5.45 | 6
3.5 | 3.89 | 4.12 | 4.38 | 4.67 | 5 | 5.22 | 5.38 | 5.83 | 6.36 | 7
4 | 4.44 | 4.71 | 5 | 5.33 | 5.71 | 5.97 | 6.15 | 6.67 | 7.27 | 8
4.5 | 5 | 5.29 | 5.63 | 6 | 6.43 | 6.72 | 6.92 | 7.5 | 8.18 | 9
5 | 5.56 | 5.88 | 6.25 | 6.67 | 7.14 | 7.46 | 7.69 | 8.33 | 9.09 | 10
5.5 | 6.11 | 6.47 | 6.88 | 7.33 | 7.86 | 8.21 | 8.46 | 9.17 | 10 | 11
6 | 6.67 | 7.06 | 7.5 | 8 | 8.57 | 8.96 | 9.23 | 10 | 10.91 | 12
6.5 | 7.22 | 7.65 | 8.13 | 8.67 | 9.29 | 9.7 | 10 | 10.83 | 11.82 | 13
7 | 7.78 | 8.24 | 8.75 | 9.33 | 10 | 10.45 | 10.77 | 11.67 | 12.73 | 14
7.5 | 8.33 | 8.82 | 9.38 | 10 | 10.71 | 11.19 | 11.54 | 12.5 | 13.64 | 15
8 | 8.89 | 9.41 | 10 | 10.37 | 11.43 | 11.94 | 12.31 | 13.33 | 14.55 | 16
8.5 | 9.44 | 10 | 10.63 | 11.33 | 12.14 | 12.69 | 13.08 | 14.17 | 15.45 | 17
9 | 10 | 10.59 | 11.25 | 12 | 12.86 | 13.43 | 13.85 | 15 | 16.36 | 18
9.5 | 10.56 | 11.18 | 11.88 | 12.67 | 13.57 | 14.18 | 14.62 | 15.83 | 17.27 | 19
10 | 11.11 | 11.76 | 12.5 | 13.33 | 14.29 | 14.93 | 15.38 | 16.67 | 18.18 | 20